## Technician OLE
No. | Category | Tool Description | Qty / Tech | Reference | Supplier | Product Link (URL) | Unit Price (€ ex-VAT) | Calibration | Frequency | Lifespan | Calib. Cost (€/yr) | Price Source | Detailed Usage
1 | Safety / PPE (HV) | HV voltage detector 25kV AC / 1500V DC – audible + visual – insulating pole mount | 1 | CATU CC-765-25-C (25kV AC) / CATU ZVATDCINDE (1500V DC) | CATU / 4NRJ | https://www.catuelec.com/produitcatu/Equipement%20de%20poste%20et%20de%20mise%20%C3%A0%20la%20terre%20et%20en%20court-circuit%20HTA/D%C3%A9tecteur%20de%20tension%20/67358/146362 | 285 | Yes | Annual (functional test + calibration) | 5 years | 95 | CATU catuelec.com – CC-765-25-C confirmed (25kV AC, catenary hook, IEC 61243-1) / ZVATDCINDE (1500V DC bipolaire) | Mandatory absence-of-voltage verification before any catenary work (25kV AC mainline/RER or 1500V DC urban networks). Used before earthing operations. Approved type per IEC 61243-3. Mounted on insulating pole. Bi-range models available per network.
2 | Safety / PPE (HV) | Class 4 (40kV) insulating gloves + leather over-gloves – pair – EN 60903 | 1 | Salisbury E416B Class 4 + AT398 leather | Honeywell Salisbury | https://www.mitchellinstrument.com/salisbury-e416b-insulated-rubber-electrical-gloves-class-4-high-voltage-gloves.html | 195 | Yes | 6 months (dielectric test IEC 60903) | Replace if failed | — | Honeywell Salisbury E416B – Class 4 (36kV max use / 40kV test) – confirmed mitchellinstrument.com ~€195 | Mandatory for catenary work on 25kV AC networks. Class 4 = protection up to 40kV. Class 2 (26kV) for 1500V DC networks. Test certificate must be current. Never handle catenary components with gloves outside validity period.
3 | Safety / PPE (HV) | Arc-rated work trousers + jacket – Category 2 – EN IEC 61482-2 | 1 | Oberon FR Arc Rated Trousers + Jacket Cat 2 | Oberon / RS Components | https://uk.rs-online.com/web/c/safety-security/personal-protective-equipment/protective-workwear/ | 245 | No | Replace if damaged | 3 years | — | Oberon / RS Components EU ex-VAT 2024 – ~€245 set | Arc-rated clothing for catenary technicians – does not burn or melt in arc flash event. Category 2 = up to 12 cal/cm². Required for all work within flash protection boundary. Worn under other PPE.
4 | Safety / PPE (HV) | Electrical Safety Helmet with Integrated Faceshield | 1 | EVO VISTAshield | JSP | https://www.jspsafety.com/products/PPE/Head-Protection/EN-397-industrial-Safety-Helmets/VAR-AMC170-007-F00_EVO-ViSTAshield-Safety-Helmet-with-integrated-Faceshield | 58 | No | Annual (visual) | 5 years | — | Simulateur baseline JSP EVO VISTAshield ? 58 ? ex-VAT | Head and face protection for OLE work at height, with integrated faceshield to improve coverage during proximity work on masts, supports and catenary structures. Chin strap mandatory at working height.
5 | Safety / PPE (HV) | Fall arrest harness full-body EN 361 + energy-absorbing lanyard 2 m + dorsal connector | 1 | 3M DBI-SALA ExoFit NEX / Petzl SEQUOIA | 3M / Petzl | https://www.petzl.com/en/Professional/Harnesses/SEQUOIA | 320 | Yes | Annual (inspection by competent person) | 10 years | — | 3M / Petzl EU ex-VAT 2024 – ~€320 | Mandatory for all catenary work at height (typically 5–9 m on aerial work platforms or fixed structures). EN 361 full-body harness + EN 355 energy absorber. Annual inspection mandatory. Replace after any fall or shock loading.
6 | Safety / PPE (HV) | Class 2 Hi-Vis jacket – retro-reflective strips – EN ISO 20471 | 1 | Portwest T830 Hi-Vis Softshell / Snickers 1148 | Portwest / Snickers | https://www.portwest.com/en-gb/collections/hi-vis-jackets | 85 | No | Annual (renewal) | 2 years | — | Portwest EU ex-VAT 2024 – ~€85 | Mandatory trackside visibility. OLE technicians work trackside, predominantly at night. EN ISO 20471 Class 2 minimum. Reinforced and waterproof for outdoor conditions.
7 | Safety / PPE (HV) | Safety boots S3 SRC – steel toecap – antistatic – insulating sole | 1 | Uvex 2 Xenova / Jalas 1688 Titanium | Uvex / Jalas | https://www.uvex-safety.com/en/products/safety-shoes/ | 145 | No | N/A | 2 years | — | Uvex / Jalas EU ex-VAT 2024 – ~€145 | Permanent PPE for OLE technicians. Antistatic sole mandatory near HV equipment. Steel toecap for trackside work. Waterproof for outdoor and night maintenance conditions.
8 | Safety / PPE (HV) | Personal LOTO kit – padlock + tags + hasp – individual – HV rated label | 1 | 65674 Personal LOTO Kit | Brady | https://www.bradyid.eu/en-eu/lockout-tagout/personal-lockout-kits/65674 | 58 | No | Annual (inspection) | 10 years | — | Simulateur baseline Brady 65674 Personal LOTO Kit ? 58 ? ex-VAT | Individual consignation of sectioning devices (interrupters, disconnectors, feeder circuit breakers) before any catenary work. Every technician holds own padlock on group hasp. HV-rated labels distinguish from LV LOTO.
9 | Safety / PPE (HV) | Knee pads ergonomic hard-shell – EN 14404 | 1 | 3M Tekk 620-00 / Portwest KP14 | 3M / Portwest | https://uk.rs-online.com/web/c/safety-security/personal-protective-equipment/knee-pads/ | 35 | No | Replace if worn | 2 years | — | 3M / RS Components EU ex-VAT 2024 – ~€35 | OLE technicians frequently work kneeling on aerial work platforms, mast foundations, and trackside walkways. EN 14404 Type 2 for hard surfaces.
10 | Messenger Wire & Droppers | Dropper length measurement tape – stainless – 3 m – catenary graduation | 2 | Lufkin / Stanley metric tape stainless 3 m | Stanley / Lufkin | https://uk.rs-online.com/web/c/tools/hand-tools/measuring-tapes/ | 25 | No | Replace if worn | 5 years | — | RS Components EU ex-VAT 2024 – ~€25 | Measurement and adjustment of dropper lengths during contact wire re-levelling. Dropper length determines presag profile at each support point. Stainless steel for outdoor use.
11 | Insulators | Insulator cleaning brush set – non-conductive bristles – 3 sizes – pole-mounted | 1 | CATU pole-mount brush set / Hubbell insulator brush | CATU / Hubbell | https://www.catu.com/en/products/ | 85 | No | Annual (visual) | 5 years | — | CATU / Hubbell EU ex-VAT 2024 – ~€85 | Periodic cleaning of catenary insulators (salt, industrial pollution, bird droppings). Non-conductive handles and bristles. Used with insulating pole for work at height. Cleaning combined with visual inspection walk.
12 | Mast & Structures | Wire brush + stainless scraper + corrosion inhibitor spray – mast treatment kit | 1 | Würth corrosion protection kit – stainless brush + Rost-Off spray | Würth | https://www.wurth.co.uk/rust-off-plus | 45 | No | N/A (consumable) | N/A | — | Würth EU ex-VAT 2024 – ~€45 kit | Rust removal and protection treatment on mast bolt holes, clamps, and connection points during PM. Annual application on mast fasteners in corrosion-prone environments (coastal, tunnels, bridges).
13 | Electrical Testing | TRMS AC/DC Clamp Meter 1000A with iFlex | 1 | 376 FC | Fluke | https://www.fluke.com/fr-fr/produit/mesure-courant/pinces-amperemetriques/fluke-376-fc | 703 | Yes | Annual | 10 years | 145 | Simulateur baseline Fluke 376 FC ? 703 ? ex-VAT | Traction return current measurement on rails and earthing conductors, bonding cable current distribution checks. 1000A range covers traction return current on urban networks. iFlex flexible probe for large conductors. Fluke Connect for data logging.
14 | Electrical Testing | Multimeter TRMS 1000V CAT IV – Fluke 289 – with temperature and logging | 1 | Fluke 289 (art.2094394) | Fluke | https://www.fluke.com/fr/produit/test-electrique/multimetres-numeriques/fluke-289 | 976 | Yes | Annual | 10 years | 130 | Fluke France price list 2025 - FLUKE-289/EUR at 976 EUR ex-VAT | HV-rated general electrical measurement (1000V CAT IV). Substation secondary voltage, bonding resistance, earthing continuity. TrendCapture logging for monitoring during energisation. Temperature measurement for joint thermal checks.
15 | Geometric Measurement | Contact wire residual thickness calliper gauge – grooved profile – EN 50149 | 1 | Bime RCWG / CATU FDC contact wire profile gauge | Bime / CATU | https://www.steinmeyer-railway.com/en/measuringdevices | 145 | Yes | Annual (calibration) | 10 years | 55 | Bime / CATU EU ex-VAT 2024 – ~€145 | Manual contact wire wear measurement at hotspots, pantograph wear bands, and section breaks. Jaw profile fits standard contact wire grooves (107, 120, 150 mm2 CuAg, CuMg). EN 50149 defines rejection thresholds. Mandatory reading at each maintenance visit on critical sections.
16 | General Hand Tools | Combination spanner set metric 8–24 mm – 13 pcs | 1 | Facom OGV 440.JP13T / Wiha 27681 insulated set | Facom / Wiha | https://www.facom.com/en-gb/products/wrenches/combination-wrenches/ | 125 | No | Replace if worn | 10 years | — | Facom / Wiha EU ex-VAT 2024 – ~€125 | Compact spanner set for catenary hardware at height: cantilever arm fixings, registration arm clamps, steady arm adjustments, dropper clamps on aerial work platform.
17 | General Hand Tools | Ratchet set 1/2" + 3/8" metric sockets – 40 pcs | 1 | Facom J.161 40pcs / Wera 9100 SB | Facom / Wera | https://www.facom.com/en-gb/products/sockets-and-ratchets/ | 125 | No | Replace if worn | 10 years | — | Facom / Wera EU ex-VAT 2024 – ~€125 | Mast hardware, clamp bolts, registration arm screws. Ratchet drive for confined spaces on platform or at mast top.
18 | General Hand Tools | VDE 1000V Insulated Screwdriver Set ? 7 pcs | 1 | 36295 SoftFinish VDE Set | Wiha | https://www.wiha.com/fr-fr/outillage/tournevis/tournevis-vde/softfinish-vde/36295/ | 78 | No | Annual (visual) | 10 years | — | Simulateur baseline Wiha 36295 SoftFinish VDE Set ? 78 ? ex-VAT | Electrical work on control panels, relay panels, earthing terminals, bonding connections at catenary structures. IEC 60900 1000V rated. Daily use during corrective and preventive maintenance.
19 | General Hand Tools | VDE 1000V Insulated Pliers Set ? 5 pcs | 1 | 00 20 12 VDE | Knipex | https://www.knipex.com/en/products/002012 | 145 | No | Annual (visual) | 10 years | — | Simulateur baseline Knipex 00 20 12 VDE ? 145 ? ex-VAT | Wiring and bonding cable work: cutting/stripping earthing cable (25–95 mm2), connector manipulation, bond clamp handling at catenary structures and relay rooms.
20 | General Hand Tools | Individual Tool Bag with shoulder strap | 1 | 00 21 02 LE Tool Bag Classic | Knipex | https://www.knipex.com/products/tool-bags-and-tool-cases/tool-bag-classic-empty/tool-bag-classic-empty/002102LE | 132 | No | Replace if worn | 5 years | — | Simulateur baseline Knipex 00 21 02 LE Tool Bag Classic ? 132 ? ex-VAT | Personal carry bag for daily catenary hand tools and small test instruments during platform, mast and access-route interventions.
21 | General Hand Tools | Hex key set metric 1.5–19 mm short + long – 22 pcs | 1 | Facom 83H.JP22 | Facom | https://www.facom.com/en-gb/products/hex-keys/ | 75 | No | Replace if worn | 10 years | — | Facom EU ex-VAT 2024 – ~€75 | Socket-head cap screws on catenary hardware: cantilever arm connections, dropper clamps, registration wire fittings, section insulator hardware.
22 | General Hand Tools | Telescopic mirror with LED – 360° pivot – inspection | 1 | Facom S.270PB telescopic inspection mirror | Facom | https://www.facom.com/en-gb/products/ | 22 | No | Replace if worn | 5 years | — | Facom EU ex-VAT 2024 – S.270PB ~€22 | Visual inspection of contact wire underside, clamp positions, section insulator back-faces, mast bolt holes inaccessible from front.
23 | Lubrication & Maintenance | Penetrating lubricant spray 400 ml – catenary hardware – lot 3 cans | 3 | Würth Rost-Off Plus / WD-40 Specialist | Würth / WD-40 | https://www.wurth.co.uk/rost-off-plus | 28 | No | N/A (consumable) | N/A | — | Würth EU ex-VAT 2024 – ~€9.50/can, €28 lot 3 | Seized mast bolts, registration arm clamps, balance weight carriages, section insulator hardware. 30–50% of hardware typically seized on outdoor structures. Apply 10 min before disassembly. Do not apply near current-carrying contact points.
24 | Lubrication & Maintenance | Silicone grease 300 g – insulator surface treatment – anti-contamination | 2 | Dow Corning DC-4 / Electrolube HVS | Dow Corning / Electrolube | https://uk.rs-online.com/web/c/adhesives-sealants-maintenance-chemicals/greases/ | 45 | No | N/A (consumable) | N/A | — | Dow / RS Components EU ex-VAT 2024 – ~€45/tub | Application to insulator creepage surfaces to repel contamination and reduce leakage current in polluted environments (coastal, industrial). Periodic treatment every 1–2 years per pollution severity class IEC 60815.
25 | Lubrication & Maintenance | Lubricant grease for tensioning pulleys and balance weight guides | 2 | Molykote G-1000 / Klüber Grease NCA 15 | Molykote / Klüber | https://uk.rs-online.com/web/c/adhesives-sealants-maintenance-chemicals/greases/ | 38 | No | N/A (consumable) | N/A | — | Molykote / RS Components EU ex-VAT 2024 – ~€38/tube | Lubrication of tensioning pulley bearings, balance weight guide rods, turnbuckles, and swivel clamps on auto-tensioning systems. Annual application at each auto-tensioning structure.
26 | Lubrication & Maintenance | Abrasive cloth 80/120/240 grit – lot 30 sheets – outdoor use | 1 | Bosch Expert C355 / Würth abrasive cloth | Bosch / Würth | https://www.bosch-professional.com/gb/en/products/ | 22 | No | N/A (consumable) | N/A | — | Bosch / Würth EU ex-VAT 2024 – ~€22 lot 30 | Contact surface preparation before bonding clamp installation, copper contact cleaning before electrical measurements, deburring cut wire ends before crimping.

## Team OLE
No. | Category | Tool Description | Qty / Team | Reference | Supplier | Product Link (URL) | Unit Price (€ ex-VAT) | Calibration | Frequency | Lifespan | Calib. Cost (€/yr) | Price Source | Detailed Usage
1 | LOTO / Safety HV | Section LOTO station – multi-lock hasp + HV disconnect keys + substation keys | 1 | Brady 148359 LOTO station + HV substation key set | Brady | https://www.bradyid.eu/en-eu/lockout-tagout/lockout-stations/ | 420 | No | Annual (inspection) | 10 years | — | Brady EU ex-VAT 2024 – ~€420 | Group isolation of catenary section disconnectors, HV feeder circuit breakers, and substation panels. Each technician places personal padlock on hasp. Manages simultaneous multi-point isolation of complex feeding arrangements.
2 | LOTO / Safety HV | HV rescue hook + resuscitation mat – insulated 10kV – EN 60900 | 1 | CATU HV Rescue Hook + mat / Salisbury HV rescue kit | CATU / Salisbury | https://www.catu.com/en/products/high-voltage/ | 285 | No | Annual (inspection) | 7 years | — | CATU EU ex-VAT 2024 – ~€285 | Emergency first-response for electrical accident involving catenary. Insulated rescue hook to remove victim from contact without direct touch. Non-conductive resuscitation mat. Mandatory emergency kit per workplace regulations.
3 | LOTO / Safety HV | 4-gas detector (O2/CO/H2S/LEL) – tunnel and confined space – Dräger X-am 2500 | 2 | 8323919 X-am 2500 4-Gas Set | Drager Safety | https://www.draeger.com/fr_fr/Products/X-am-2500 | 995 | Yes | Annual (gas calibration) | 5 years | 195 | Simulateur baseline Drager 8323919 X-am 2500 4-Gas Set ? 995 ? ex-VAT | Atmospheric monitoring for catenary work in tunnels, confined substation rooms, and cable trenches. CO/O2 monitoring in rail tunnels where diesel maintenance vehicles have operated. Continuous monitoring during confined-location access.
4 | Advanced Measurement | Thermal Imaging Camera 320x240 radiometric | 1 | TiS60+ | Fluke | https://www.fluke.com/fr-fr/produit/cameras-thermiques/fluke-tis60-plus | 3812 | Yes | Annual (COFRAC) | 8 years | 380 | Simulateur baseline Fluke TiS60+ ? 3812 ? ex-VAT | Thermal inspection of catenary connection points, feeder joints, section insulators, substation busbars during de-energised possession. Identifies resistive hot spots. Also used for mast bonding and balance weight brake checks.
5 | Messenger Wire & Droppers | Come-along cable puller / chain hoist 1.5 t – insulated handles – wire tensioning | 1 | Tractel Tirfor T-516 / Yale CLX 1.5t | Tractel / Yale | https://www.tractel.com/en/products/hoists-and-pullers/ | 485 | No | Annual (inspection + load test) | 10 years | — | Tractel EU ex-VAT 2024 – ~€485 | Tensioning messenger wire and contact wire during re-tensioning operations, wire replacement, and span repairs. Requires min. 2 operators. Insulated handles for proximity HV work. Attached to platform anchor points during team operations.
6 | Workshop / Team | Mobile Workshop Roller Cabinet 6 drawers | 1 | RSC24A/6 | Beta Tools | https://www.beta-tools.com/en/mobile-roller-cab-with-6-drawers-with-anti-tilt-system.html | 669 | No | Replace if worn | 10 years | — | Simulateur baseline Beta Tools RSC24A/6 ? 669 ? ex-VAT | Shared team roller cabinet with drawers for OLE instruments, gauges, consumables and work-front equipment in a standardised workshop format.
7 | Workshop / Team | Portable inverter generator 2kVA – silent – 230V – night maintenance | 1 | Honda EU22i / Yamaha EF2200iS | Honda / Yamaha | https://www.honda.co.uk/power-products/generators/eu22i.html | 1250 | No | Annual (service) | 7 years | — | Honda / Yamaha EU ex-VAT 2024 – EU22i ~€1250 | Power supply for battery tool charging on remote catenary sections, portable lighting during night possessions, laptop and measuring equipment. Silent inverter type for night maintenance windows. Carried on team vehicle.
8 | Workshop / Team | Portable LED floodlights 100W – tripod – IP65 – night possession work | 2 | Peli 9430 RALS / Brennenstuhl 1178800003 | Peli / Brennenstuhl | https://www.peli.com/en/product/lights/remote-area-lighting/ | 285 | No | Annual (lamp check) | 7 years | — | Peli / Brennenstuhl EU ex-VAT 2024 – ~€285 | Area lighting for catenary maintenance during night possessions (standard OLE working window). IP65 outdoor rated. Tripod-mounted for hands-free working. Two units provide adequate lighting for a single-span work zone.
9 | Contact Wire | Battery hydraulic tool kit – cutter + kink remover – BDL41 handle + CS.25-B cutter head + XDH41 straightener head | 1 | Stanley Dubuis BDL41 + CS.25-B + XDH41 complete kit | Stanley Dubuis | https://www.powerandcables.com/catenary-wire-straighteners-tools-to-remove-kinks-from-overhead-rail-cables/ | 2850 | Yes | Annual (pressure + blades + function test) | 7 years | 185 | Stanley Dubuis EU ex-VAT 2024 – BDL41 handle + CS.25-B + XDH41 ~€2850 complete kit | Single battery hydraulic handle (BDL41, 18V DeWalt/Stanley) with 2 interchangeable heads: CS.25-B cutter head (clean Ø25mm contact wire cut, no deformation) + XDH41 straightener head (kink removal without cutting). Rotating head 180° for difficult angles. SNCF homologated. NB: handle shared – only one operation at a time.
10 | Contact Wire | Contact wire tension dynamometer – 0–30 kN – hook-on type – COFRAC | 1 | Dynafor Pro 1T - code 293369 | Tractel | https://www.tractel.com/PIM/TBN_products/Price-list-pdf/2025/TBN-pricelist-2025-EN.pdf | 1874 | Yes | Annual (COFRAC) | 10 years | 120 | Tractel 2025 price list - Dynafor Pro 1T code 293369 at 1874 EUR ex-VAT | Verification of contact wire mechanical tension after section repair, balance-weight adjustment and temperature-related retensioning, using a compact traceable lifting dynamometer in the relevant OLE load range.
11 | Geometric Measurement | Portable laser height and stagger gauge – ±3 mm accuracy – IP54 – standalone | 1 | Steinmeyer FM4-LO / Paragon ABT4640 Metal | Steinmeyer / Paragon | https://www.steinmeyer-railway.com/en/measuringdevices/contact-wire-height-and-contact-wire-position | 2800 | Yes | Annual (calibration) | 10 years | 250 | Steinmeyer / Paragon EU ex-VAT 2024 – FM4-LO ~€2800 | Manual measurement of contact wire height (above rail level) and stagger (lateral offset) at each structure and midspan. EN 50119 defines limits (height 4700–6200mm, stagger ±200–300mm per network spec). Laser-based – no contact with wire. Data stored for maintenance register.
12 | Earthing & Bonding | Portable earthing + short-circuit set 25kV / 1500V DC – catenary clamp + rail clamp + copper braid | 1 | CATU CT-246 / Stanley Dubuis TPU + MPR set | CATU / Stanley Dubuis | https://industrialtoolsandattachments.com/products/catenary-maintenance | 650 | Yes | Annual (visual + resistance test) | 10 years | 120 | CATU / Stanley EU ex-VAT 2024 – ~€650 complete set | Critical safety equipment – mandatory after voltage detector confirms de-energisation. Shorts and earths the catenary wire to the running rail. Icc rated per network fault current (12kA/150ms for 25kV AC, 35kA/25ms for 1500V DC). Includes rail foot clamp MPR + catenary clamp + copper braid.
13 | Earthing & Bonding | Insulating telescopic pole 3–8 m – 25kV homologated – reinforced fibreglass | 2 | CATU PM-252 / Stanley Dubuis PITR | CATU / Stanley Dubuis | https://industrialtoolsandattachments.com/products/catenary-maintenance | 285 | Yes | Annual (dielectric test + visual) | 10 years | 95 | CATU / Stanley EU ex-VAT 2024 – ~€285 | Placement of earthing sets, voltage detector and bonding cable on catenary wire from ground or platform. Telescopic for transport. 25kV homologated. Min. 2 poles per technician (one for catenary clamp, one for rail-catenary bonding).
14 | Contact Wire | Contact wire self-locking clamp pliers – autolock – contact wire groove fit | 2 | CATU PF-602 / Stanley Dubuis pince fil de contact | CATU / Stanley Dubuis | https://galland-sas.com/wp-content/uploads/2024/08/GALLAND-CATALOGUE-OUTILLAGE-2020.pdf | 95 | No | Annual (visual) | 7 years | — | CATU / Galland EU ex-VAT 2024 – ~€95 | Holding and repositioning contact wire during clamp replacement, dropper fitting, and kink repair without releasing wire tension. Auto-locking jaw grips grooved copper wire securely. 2 per technician for clamping either side of work zone.
15 | Messenger Wire & Droppers | Battery hydraulic crimping tool – 50–240 mm2 – die set for catenary connectors | 1 | CATU TTMH-S-240 / Stanley Dubuis crimping tool | CATU / Stanley Dubuis | https://galland-sas.com/wp-content/uploads/2024/08/GALLAND-CATALOGUE-OUTILLAGE-2020.pdf | 2450 | Yes | Annual (pressure calibration + dies) | 7 years | 185 | CATU / Stanley EU ex-VAT 2024 – ~€2450 | Hydraulic crimping of catenary connectors and terminations on messenger wire (70–185 mm2 CuCd/BzII), contact wire joints, and feeder cable lugs. Battery-powered for mobility on platform. Die set covers all standard catenary sections. SNCF homologated dies available.
16 | Mast & Structures | Torque wrench 1/2" 20–200 Nm + 3/4" 100–600 Nm – COFRAC cert. | 1 | Facom S.307-200 + S.309-600 COFRAC | Facom | https://www.facom.com/en-gb/products/tightening-and-torque/torque-wrenches/ | 575 | Yes | Annual (COFRAC) | 10 years | 165 | Facom EU direct ex-VAT 2024 – set ~€575 | Controlled torque on mast bolts (M16–M30 foundation bolts, cantilever arm fixings), registration arm hardware, steady arm clamps. Torque values per OLE design drawings. Traceable calibration mandatory for safety-critical fixings per EN 50119.
17 | Mast & Structures | Digital Protractor / Clinometer Pro 360 - 0 to 360 deg | 1 | Mitutoyo 950-317 Pro 360 | Mitutoyo | https://www.newark.com/es/mitutoyo/950-317/digital-protractor-0-360deg/dp/82K5524 | 443 | Yes | Annual | 7 years | 55 | Mitutoyo distributor price list 2023 (Saratools) - 950-317 at 443 EUR ex-VAT | Mast verticality and cantilever-angle verification after installation, vehicle strike, settlement or adjustment, using a portable digital inclinometer with full 360-degree range.
18 | Geometric Measurement | Laser distance meter 0.05–200 m ±1 mm – IP54 – tilt sensor – Leica DISTO D5 | 1 | Leica DISTO D5 (ref 803067) | Leica Geosystems | https://shop.leica-geosystems.com/fr-FR/measurement-tools/disto/leica-disto-d5/buy | 520 | Yes | Annual | 8 years | 90 | Leica official D5 shop page plus current official UK shop pricing; workbook value normalised to approx. 520 EUR ex-VAT | Span length measurement, mast spacing, clearance checks to structures (bridges, tunnels, platforms). Tilt sensor for angled distances. Bluetooth data transfer to tablet. Used for geometry surveys and clearance audits.

## Project OLE
No. | Category | Tool Description | Qty / Depot | Reference | Supplier | Product Link (URL) | Unit Price (€ ex-VAT) | Calibration | Frequency | Lifespan | Calib. Cost (€/yr) | Price Source | Detailed Usage
1 | Advanced Measurement | Portable catenary geometry survey trolley – height + stagger + wear – laser + camera | 1 | Steinmeyer FM8 / 4NRJ VISIOCAT / tCat trolley | Steinmeyer / 4NRJ | https://tcat.es/english-measuring-the-height-and-stagger-of-a-contact-wire/ | 18500 | Yes | Annual (calibration) | 10 years | 850 | Steinmeyer / 4NRJ EU ex-VAT 2024 – ~€18500 | Complete portable geometry survey system: contact wire height ±3mm, stagger ±5mm, residual thickness (wear), track gauge, cant. Pushed along track during possession window. Produces full geometry report for maintenance register. Used for periodic VLC campaigns and before/after major works.
2 | Earthing & Bonding | Earth resistance tester – 3-electrode method – 0.01–2000 Ω – IEC 61557-5 | 1 | CA 6470N - P01126506 | Chauvin Arnoux | https://fr.rs-online.com/web/p/testeurs-de-terre/7059286 | 1948.29 | Yes | Annual | 8 years | 110 | RS France 705-9286 - Chauvin Arnoux CA 6470N P01126506 at 1948.29 EUR ex-VAT | Measurement of mast earthing resistance (EN 50122-1: typically <1 Ω for metallic structures in HV zone). Post-repair earthing verification. Also for rail bonding and station earthing checks.
3 | Advanced Measurement | Digital Lifting Dynamometer 0-65 kN | 1 | Dynafor Pro 6.5t | Tractel | https://www.tractel.com/en/products/load-monitoring-instrumentation/dynamometers/ | 2850 | Yes | Annual (COFRAC) | 10 years | 320 | Simulateur baseline Tractel Dynafor Pro 6.5t ? 2850 ? ex-VAT | Project/depot lifting dynamometer for proof-load checks, structural pulling operations and traceable load verification on heavy OLE maintenance or commissioning campaigns.

## Codex Wave 1
CAT Tooling Review | Wave 1 expert utility review only. No source sheets modified yet.
Overall verdict | Good OLE maintenance base, but Technician OLE is over-scoped. Several useful items are not realistic as 1 per tech and should move to Team or Project.
Key themes | 1) lighten Technician sheet, 2) remove duplicated hand-tool logic, 3) mark tunnel/pollution-specific items as conditional, 4) move heavy survey/tension tooling upward.
Source sheet | No. | Tool description | Assessment | Recommended action | Rationale
Technician OLE | 9 | Knee pads ergonomic hard-shell ? EN 14404 | Useful but conditional | Keep, but Optional / context-based | Helpful for prolonged kneeling on platforms or mast foundations, but not core OLE capability.
Technician OLE | 10 | Portable earthing + short-circuit set 25kV / 1500V DC | Critical but misallocated | Move to Team | Safety-critical equipment should be team-controlled, maintained and serialized rather than 1 per tech.
Technician OLE | 11 | Insulating telescopic pole 3?8 m | Critical but misallocated | Move to Team | Shared HV access equipment paired with detectors/earthing sets; not realistic as personal allocation.
Technician OLE | 12 | Contact wire self-locking clamp pliers | Useful but misallocated | Move to Team | Operational work-zone tooling, normally shared on platform team interventions rather than per individual.
Technician OLE | 14 | Battery hydraulic crimping tool 50?240 mm2 | Useful but misallocated | Move to Team | High-cost specialist hydraulic tool with dies and calibration/pressure checks; not individual issue.
Technician OLE | 15 | Insulator cleaning brush set | Conditional | Keep only if in-house insulator cleaning is in scope | Useful for pollution-control maintenance, but not universal across OLE contracts.
Technician OLE | 16 | Torque wrench set 1/2 + 3/4 | Useful but misallocated | Move to Team | Traceable torque tooling is shared calibrated equipment, not a per-tech baseline.
Technician OLE | 17 | Digital clinometer + spirit level | Useful but misallocated | Move to Team | Useful for mast checks, but team survey/control tool rather than daily personal tool.
Technician OLE | 19 | Combination spanner set + socket set | Functional duplicate | Remove / replace by #24 + #25 | Hand-tool coverage already provided more cleanly by dedicated spanner set and ratchet socket set.
Technician OLE | 23 | Laser distance meter Leica DISTO D5 | Useful but misallocated | Move to Team | Good survey aid, but not a daily personal OLE tool for every technician.
Technician OLE | 30 | Telescopic mirror with LED | Useful but secondary | Keep as Optional | Helpful inspection aid, but not core capability.
Technician OLE | 32 | Silicone grease 300 g ? insulator surface treatment | Conditional | Keep only if pollution-treatment policy exists | Application depends on network contamination strategy and may not be in standard team scope.
Team OLE | 3 | 4-gas detector Dr?ger X-am 2500 | Conditional | Keep only for tunnels/confined-space scope | Strongly justified for tunnels/trenches/substation rooms, not universal for open-line catenary work.
Team OLE | 6 | 7-drawer locking tool cabinet | Support workshop item | Keep only if full workshop baseline wanted | Useful depot support, but not an OLE-critical field capability.
Team OLE | 7 | Cable pull dynamometer 0?50 kN | Useful but heavy-scope | Move to Project | Campaign/re-tensioning/structural-load measurement tool, closer to project/depot scope than routine team kit.
Project OLE | 1 | Portable catenary geometry survey trolley | Clearly justified | Keep in Project | Fits project/depot survey campaigns and before/after works verification.
Project OLE | 2 | Earth resistance tester | Clearly justified | Keep in Project | Fits mast earthing verification, post-repair checks and depot-level expert measurement.

## Codex Wave 2
CAT Tooling Review | Wave 2 applied: reclassement executed in source sheets and duplicate removed.
Resulting active counts | Technician OLE: 26 ¦ Team OLE: 18 ¦ Project OLE: 3
Backup | CAT_tooling_V1_pre_codex_wave2_20260403.xlsx
Source sheet | Original No. | Tool description | Action | Destination | Reason
Technician OLE | 10 | Portable earthing + short-circuit set 25kV / 1500V DC ? catenary clamp + rail clamp + copper braid | Move | Team OLE | Useful tool but not realistic as 1 per tech
Technician OLE | 11 | Insulating telescopic pole 3?8 m ? 25kV homologated ? reinforced fibreglass | Move | Team OLE | Useful tool but not realistic as 1 per tech
Technician OLE | 12 | Contact wire self-locking clamp pliers ? autolock ? contact wire groove fit | Move | Team OLE | Useful tool but not realistic as 1 per tech
Technician OLE | 14 | Battery hydraulic crimping tool ? 50?240 mm2 ? die set for catenary connectors | Move | Team OLE | Useful tool but not realistic as 1 per tech
Technician OLE | 16 | Torque wrench 1/2" 20?200 Nm + 3/4" 100?600 Nm ? COFRAC cert. | Move | Team OLE | Useful tool but not realistic as 1 per tech
Technician OLE | 17 | Digital clinometer + spirit level ? mast verticality check ? 0?90? ?0.1? | Move | Team OLE | Useful tool but not realistic as 1 per tech
Technician OLE | 19 | Combination spanner set metric 8?24 mm + socket set 50 pcs | Delete duplicate | ? | Coverage already provided more cleanly by dedicated spanner set and ratchet socket set
Technician OLE | 23 | Laser distance meter 0.05?200 m ?1 mm ? IP54 ? tilt sensor ? Leica DISTO D5 | Move | Team OLE | Useful tool but not realistic as 1 per tech
Team OLE | 7 | Cable pull dynamometer 0?50 kN ? COFRAC ? wire tensioning campaigns | Move | Project OLE | Heavy campaign / commissioning measurement rather than routine team kit

## Codex Wave 3
CAT Tooling Review | Wave 3 applied: direct harmonisation with already validated simulator references, links and prices.
Backup | CAT_tooling_V1_pre_codex_wave3_20260403.xlsx
Approach | Only tools already covered by the simulator were standardised here, to avoid re-validating the same product twice.
Sheet | No. | Tool | Action
Technician OLE | 4 | Safety helmet EN 397 dielectric + integral face shield + chin strap | Aligned to existing simulator reference JSP EVO VISTAshield
Technician OLE | 8 | Personal LOTO kit – padlock + tags + hasp – individual – HV rated label | Aligned to existing simulator Brady personal LOTO kit
Technician OLE | 13 | TRMS clamp meter 1000A AC/DC – CAT IV – Fluke 376 FC | Aligned to existing simulator Fluke 376 FC
Technician OLE | 18 | VDE 1000V insulated screwdriver set – 7 pcs – EN 60900 | Aligned to existing simulator Wiha screwdriver set
Technician OLE | 19 | VDE 1000V plier set – combination + diagonal + stripping – 5 pcs | Aligned to existing simulator Knipex pliers set
Technician OLE | 20 | Individual tool bag – shoulder strap + platform hook – OLE rated | Replaced mixed bag reference with standard simulator tool bag
Team OLE | 3 | 4-gas detector (O2/CO/H2S/LEL) – tunnel and confined space – Dräger X-am 2500 | Aligned to existing simulator Drager X-am 2500 set
Team OLE | 4 | Thermal imaging camera 320×240px – COFRAC – connection and feeder inspection | Aligned to existing simulator Fluke TiS60+
Team OLE | 6 | 7-drawer locking tool cabinet – rolling – calibrated instrument storage | Replaced Stanley cabinet with standard simulator roller cabinet
Project OLE | 3 | Cable pull dynamometer 0–50 kN – COFRAC – wire tensioning campaigns | Replaced mixed 50 kN reference with standard simulator Dynafor Pro 6.5t

## Codex Wave 4
CAT Tooling Review | Wave 4 applied: only high-confidence OLE-specific price/reference corrections.
Backup | CAT_tooling_V1_pre_codex_wave4_20260403.xlsx
Residual note | Some OLE lines remain quote-based or network-specific and were intentionally left unchanged in this wave.
Sheet | No. | Tool | Action
Technician OLE | 14 | Multimeter TRMS 1000V CAT IV – Fluke 289 – with temperature and logging | Corrected under-valued price to current Fluke France list
Team OLE | 10 | Contact wire tension dynamometer – 0–30 kN – hook-on type – COFRAC | Replaced estimate with official Tractel 2025 price-list entry
Team OLE | 17 | Digital Protractor / Clinometer Pro 360 - 0 to 360 deg | Corrected weak reference to Mitutoyo 950-317 Pro 360 and updated price basis
Team OLE | 18 | Laser distance meter 0.05–200 m ±1 mm – IP54 – tilt sensor – Leica DISTO D5 | Raised price from a low estimate to a current official-shop equivalent
Project OLE | 2 | Earth resistance tester – 3-electrode method – 0.01–2000 Ω – IEC 61557-5 | Corrected severely under-valued price using current RS France listing