## Technician MEP
No. | Category | Tool Description | Qty / Tech | Reference | Supplier | Product URL | Unit Price (€ ex-VAT) | Calibration | Frequency | Lifespan | Calib. Cost (€/yr) | Price Source | Detailed Usage
1 | Safety / PPE | Personal LOTO kit – padlock + insulated hasp + tags – electrical isolation | 1 | 120886 | Brady | https://www.bradyid.com/products/personal-lockout-kit-electrical-pid-120886 | 109 | No | Annual (inspection) | 10 years | — | Simulator baseline aligned with Brady 120886 personal electrical LOTO kit | Mandatory isolation of LV/MV circuits before any work on fan motors, lighting panels, escalator drive cabinets, HVAC units, and pump controls. Each technician applies their own personal padlock – no shared LOTO. Tags bilingual EN/FR. Used at every corrective and preventive intervention on powered equipment.
2 | Safety / PPE | 4-gas personal monitor – O₂, CO, H₂S, LEL – confined space & tunnel entry | 1 | Dr?ger X-am 2500 Ex/O2/CO/H2S | Dr?ger | https://www.draeger.com/fr_fr/Products/X-am-2500 | 335 | Yes | 6-month (bump test) / Annual (calibration) | 5 years | 120 | Dr?ger Safety catalogue 2023/2025 for X-am 2500 Ex/O2/CO/H2S kit | Mandatory for entry into tunnel ventilation shafts, underground sump pump chambers, confined spaces below grade, and gas boiler plant rooms. Monitors O₂ (deficiency in poorly ventilated shaft), CO (diesel/exhaust ingress and gas boiler flue spillage – replaces standalone CO clip-on), H₂S (sump/drainage), and LEL (flammable gas). Continuous wear during any work in confined or gas-risk spaces. Alarm at O₂ <19.5%, CO >25 ppm TWA, H₂S >5 ppm, LEL >10%. This single instrument covers all 4-gas monitoring needs across MEP domains.
3 | Safety / PPE | Electrical insulating gloves Class 0 (1000V) + leather protector – LV panel work | 2 | Ansell ActivArmr RIG014B Class 0 + leather protector | Ansell | https://www.ansell.com/int/en/products/activarmr-electrical-insulating-gloves-class-0-rig014b | 85 | Yes | 6-month (dielectric test) | 1 year | 45 | Ansell official RIG014B product page; price kept as planning estimate for glove + leather protector set | Protection during live-panel work on lighting distribution boards, fan VFD cabinets (up to 400V AC), HVAC control panels, and pump starters. Class 0 rated to 1000V AC/1500V DC. Leather protector worn over gloves to prevent puncture. Inspection before each use for cuts, ozone cracking, or swelling. Replace annually regardless of condition.
4 | Safety / PPE | Safety glasses EN166 + EN812 bump cap + steel-toe ankle boots EN ISO 20345 | 1 | Bolle Safety COBRA COBPSI / Portwest PS59 AirTech / PUMA Safety KRYPTON MID 634200 | Bolle Safety / Portwest / PUMA Safety | https://www.bollesafety.com/en-int/sport/cobra | 159.39 | No | Replace if damaged | 1 year | — | Simulator baseline assembled from validated PPE references: Bolle COBRA + Portwest PS59 + PUMA KRYPTON MID | Baseline PPE for all MEP maintenance activities. Safety glasses for work near rotating fan blades, electrical arcing risk, and chemical cleaning. Bump cap for work inside escalator machine rooms and low-clearance plant rooms. Steel-toe boots for work around pumps, pipe fittings, and heavy fan assemblies.
5 | Electrical Measurement | TRMS digital multimeter 1000V CAT III – AC/DC voltage, current, resistance, continuity | 1 | Fluke 87V Industrial Multimeter | Fluke | https://www.fluke.com/en-gb/product/electrical-testing/digital-multimeters/fluke-87v | 495 | Yes | Annual (COFRAC) | 10 years | 95 | Fluke EU ex-VAT 2024 – 87V ~€495 | Primary electrical diagnostic tool across all MEP domains. Measures motor supply voltages (3×400V fans, escalator drives), lighting circuit voltage (230V single-phase), HVAC control signal voltages (0-10V analogue, 24V DC BMS), and continuity of earth bonds. TRMS for VFD output waveforms. Used at every corrective and preventive maintenance intervention.
6 | Electrical Measurement | AC/DC clamp meter TRMS 600A – motor and pump current draw measurement | 1 | 376 FC | Fluke | https://www.fluke.com/fr-fr/produit/mesure-courant/pinces-amperemetriques/fluke-376-fc | 703 | Yes | Annual (COFRAC) | 10 years | 120 | Simulator baseline aligned with Fluke 376 FC | Non-invasive current measurement on fan motors (typically 2–50A depending on size), escalator traction motors (10–80A), sump pump motors (1–15A), and HVAC compressors. Abnormal current draw indicates mechanical overload, bearing failure, or electrical fault. FC wireless logging for motor run-up and trending. Compares against nameplate FLA (Full Load Ampere) rating.
7 | Electrical Measurement | Non-contact voltage detector 90–1000V AC – safe live/dead verification | 1 | Fluke 2AC / Fluke T5-1000 | Fluke | https://www.fluke.com/en-gb/product/electrical-testing/voltage-testers/fluke-2ac | 28 | No | Annual (functional check) | 5 years | — | Fluke EU ex-VAT 2024 – 2AC ~€28 | Quick live/dead confirmation on lighting circuits, fan MCBs, and pump starters before connecting instruments or making contact. Used as first step before multimeter measurement – faster than probing. Mandatory first verification even when isolation has been applied (verification that LOTO was correctly executed).
8 | Plumbing & Sump Pumps | Basic pipe wrench set + basin wrench + adjustable spanner – depot plumbing | 1 | Ridgid 31305 2-pipe wrench set 250+350mm / Bahco adjustable spanner | Ridgid / Bahco | https://www.ridgid.com/eu/en/pipe-wrenches | 95 | No | Replace if worn | 10 years | — | Ridgid / Bahco EU ex-VAT 2024 – ~€95 set | Mechanical pipe work on depot distribution mains and sump pump discharge connections. Ridgid pipe wrenches for BSP threaded steel or stainless fittings (G½ to G2). Basin wrench for reaching behind-wall isolating valves on depot sanitary fixtures. Adjustable spanner for compression fittings and pump flange bolts. Core plumbing toolset for Level 2–3 corrective maintenance.
9 | Electrical Measurement | Safety VAT bipolar absence-of-voltage tester 12-1000V AC/DC ? formal prove-dead before contact | 1 | Chauvin Arnoux C.A 773 | Chauvin Arnoux | https://www.chauvin-arnoux.com/en/node/9325 | 290 | Yes | Annual (calibration) | 10 years | 65 | Simulator baseline aligned with formal IEC 61243-3 VAT tester | Mandatory formal absence-of-voltage verification before contact on isolated lighting circuits, fan starters, pump panels, escalator control panels and HVAC distribution boards. Complements the non-contact detector, which is only a first screening tool and not the final safety proof.

## Team MEP
No. | Category | Tool Description | Qty / Team | Reference | Supplier | Product URL | Unit Price (€ ex-VAT) | Calibration | Frequency | Lifespan | Calib. Cost (€/yr) | Price Source | Detailed Usage
1 | Refrigeration & HVAC (Team) | Digital manifold gauge set HP/LP + 3 hoses – refrigerant circuit diagnosis | 1 | Testo 550i digital manifold / Rothenberger RM 4 | Testo / Rothenberger | https://www.testo.com/en-GB/testo-550i/p/0564-5501 | 485 | Yes | Annual (calibration) | 7 years | 95 | Testo EU ex-VAT 2024 – 550i ~€485 | Refrigerant circuit diagnosis on split AC units and close-control units: measures HP (high-pressure / condensing), LP (low-pressure / evaporating), computes superheat and subcooling against target values for the specific refrigerant. Identifies undercharge (low LP), overcharge (high HP), dirty condenser (elevated condensing pressure), or TXV malfunction. F-gas Category I certificate mandatory. Bluetooth logging to tablet. Used at Level 2–3 refrigerant circuit interventions.
2 | Refrigeration & HVAC (Team) | Two-stage vacuum pump 71 L/min + micron gauge – evacuation before refrigerant charge | 1 | Robinair 15301 / JB DV-85N | Robinair / JB Industries | https://robinair.com/sites/default/files/documents/556679_en_rev_e_1.pdf | 485 | No | Annual (oil change + inspection) | 5 years | — | Robinair official 2-stage pump datasheet for 15301 (71 l/min); price kept as planning estimate | Deep vacuum evacuation of refrigerant circuits after opening for component replacement (compressor, TXV, drier). Target vacuum <200 microns (266 Pa) to remove residual moisture that would form acid and damage the compressor. Two-stage design achieves lower ultimate vacuum than single-stage. Micron gauge (separate) confirms vacuum level – visual gauge on pump is not accurate enough. F-gas Category I certificate required. Used at Level 3 refrigerant circuit interventions.
3 | Refrigeration & HVAC (Team) | Refrigerant electronic scale 50 kg + tare function – charge weight measurement | 1 | Fieldpiece SRS2 / Rothenberger refrigerant scale 60 kg | Fieldpiece / Rothenberger | https://www.fieldpiece.com/products/refrigerant-scale-with-wireless-jack-system-srs2/ | 285 | Yes | Annual (calibration) | 7 years | 55 | Fieldpiece EU ex-VAT 2024 – SRS2 ~€285 | Precise measurement of refrigerant charge quantity during recovery and recharge. F-gas regulation requires recording of refrigerant quantities recovered and recharged by weight (not by pressure alone). Resolution 5g for accurate charging to OEM specification (±50g tolerance typical). Wireless display allows technician to monitor from manifold gauge position. Used with manifold gauge set for complete refrigerant circuit service.
4 | Refrigeration & HVAC (Team) | Coil cleaning pressure sprayer + coil cleaner chemicals – condenser/evaporator PM | 1 | Jetwave sprayer 12L / Nu-Brite coil cleaner + Coil Frost non-acid evaporator cleaner | Various | https://uk.rs-online.com/web/c/hvac-r/air-conditioning-components/ | 145 | No | N/A (consumable) | N/A | — | HVAC supplier EU ex-VAT 2024 – ~€145 kit | Condenser and evaporator coil cleaning at PM inspection intervals (typically annual). Dirty condenser coils increase condensing pressure, reduce compressor efficiency, and increase energy consumption by 10–25%. Non-acid evaporator cleaner protects aluminium fins from chemical attack. Low-pressure rinsing with pH-neutral cleaner, foaming agent applied and rinsed. Used at Level 2–3 PM on all AC units in traction substations and signalling rooms.
5 | Heating (Team) | Hydraulic pipe pressure test pump 0–40 bar – heating system pressure test | 1 | Rothenberger RP50-S / Rothenberger Super Test II | Rothenberger | https://rothenberger.com/it-it/pompe-provaimpianti-per-tubazioni-di-acqua/pompa-di-prova-rp-50-s-60200/ | 485 | Yes | Annual (calibration) | 7 years | 85 | ROTHENBERGER official product page RP 50-S; price kept as planning estimate | Pressure testing of heating circuit pipework after Level 2–3 repair or extension (new radiator run, heat exchanger replacement, valve bypass). Test pressure per BS 7593 / EN 806: 1.5× maximum working pressure held 1 hour minimum with no visible drop. Hydraulic pump ensures stable pressure without gas compression risk. Includes 100-litre capacity for large heating systems. Results recorded in CMMS as compliance evidence.
6 | Plumbing (Team) | Electric drain cleaning machine – 25m cable – Level 2–3 drain blockage clearance | 1 | Ridgid K-45 / Rothenberger Rospidomatic 22 | Ridgid / Rothenberger | https://www.ridgid.com/eu/en/k-45 | 685 | No | Annual (cable inspection) | 7 years | — | Ridgid EU ex-VAT 2024 – K-45 ~€685 | Mechanical clearance of blocked depot drainage, inspection chamber pipes, and sump pump inlets. Rotating cable with cutter head breaks through grease blockages, root intrusions, and accumulated solids. 25m cable reach covers most depot drain runs. Used at Level 2 for reactive drain blockage calls and at Level 3 for planned drain cleaning campaigns. PPE requirement: face shield, heavy-duty gloves, waterproof oversuit.
7 | Plumbing (Team) | Pipe freeze kit CO₂ – 15–54mm copper – pipe isolation without system drain-down | 1 | Rothenberger Rofrost Turbo / Hilmor Freeze Kit | Rothenberger / Hilmor | https://www.rothenberger.com/en_GB/products/pipe-installation/pipe-freezing/rofrost-turbo | 485 | No | Annual (cylinder inspection) | 7 years | — | Rothenberger EU ex-VAT 2024 – Rofrost Turbo ~€485 | Localised pipe isolation by forming an ice plug in copper pipe (15–54mm OD) without draining the entire heating or water circuit. Used for valve replacement, pipe repair, or new connection without full system shutdown – critical at depot where full heating drain-down would take 4–8 hours and require system refill and inhibitor dosing. CO₂ cartridges form plug in 5–15 minutes depending on pipe diameter. Suitable for water and low-pressure heating circuits only.
8 | Workshop / Team | Mobile workshop trolley 7 drawers – dedicated MEP tool storage and organisation | 1 | Stanley FMST1-75797 FatMax 7-drawer / Facom JET.7GR | Stanley / Facom | https://www.stanleytools.com/ | 585 | No | Replace if worn | 10 years | — | Stanley / Facom EU ex-VAT 2024 – ~€585 | Dedicated MEP tool storage in depot maintenance workshop. Drawers organised by domain: electrical measurement, HVAC/refrigeration, plumbing, escalator tools. Calibrated tools stored in foam-lined drawer with calibration due-date label visible without removing tool. Mobile for deployment to station or specific plant room. Prevents loss of calibrated tools and keeps MEP specialist equipment separate from general maintenance toolkit.
9 | Workshop / Team | Rugged Android tablet + CMMS app – work order management and asset history | 1 | Panasonic TOUGHBOOK A3 / Getac T800 rugged tablet | Panasonic / Getac | https://eu.connect.panasonic.com/sites/default/files/media/document/2023-01/TOUGHBOOK_A3_Spec_Sheet_%281%29_1664202692.7016%20%281%29.pdf | 1450 | No | 5-year (replacement cycle) | 5 years | — | Panasonic TOUGHBOOK A3 current official spec sheet; price kept as planning estimate | Real-time work order entry and closure in CMMS (Maximo, SAP PM, CARL Source, or network-proprietary system). Access to MEP asset maintenance history, OEM manuals, and inspection checklists. QR/barcode scanning for rapid asset identification (fan units, escalators, HVAC units). Wi-Fi synchronisation for live update of maintenance records. Critical for Level 2–3 interventions requiring audit trail (EN 115 escalator dossier, F-gas refrigerant log, Gas Safe certificate record).
10 | Electrical Measurement | Insulation resistance tester 500V / 1000V DC (megohmmeter) – motor winding check | 1 | 1507 Insulation Tester | Fluke | https://www.fluke.com/fr-fr/produit/testeurs-isolement/fluke-1507 | 699 | Yes | Annual (calibration) | 10 years | 85 | Simulator baseline aligned with Fluke 1507 | Motor winding insulation test before recommissioning after rewinding or flood exposure. Tests fan motor windings, pump motor windings, and escalator traction motor insulation. Minimum acceptable: 1 MΩ at 500V (low confidence) ; >100 MΩ healthy motor. Also used for cable insulation verification after maintenance on buried or conduit runs. PI (Polarisation Index) test available for trending.
11 | Tunnel Ventilation | Air flow meter kit with differential pressure + vane probes ? duct and grille airflow measurement | 1 | testo 440 dP Air Flow ComboKit 2 (0563 4410) | Testo | https://www.testo.com/en-UK/testo-440-delta-p-air-flow-combokit-2-with-bluetooth-r/p/0563-4410 | 1935 | Yes | Annual (calibration) | 7 years | 85 | Testo official UK price 1655 GBP ex VAT for 0563 4410; converted indicative planning estimate to EUR | Measurement of airflow velocity and volume flow in tunnel ventilation ducts and at fan discharge/suction. Verifies fan performance against design specification (typically 2–25 m/s in tunnel). Pitot tube for duct traversal measurements per EN 15780. Identifies fan blade fouling (reduced flow), damper malfunction (incorrect DP), or drive speed drift. Used at each PM inspection and after fan replacement.
12 | Tunnel Ventilation | Portable vibration meter – bearing and motor housing – ISO 10816 Level 1-2 | 1 | Fluke 805 FC / SKF CMAS 100-SL | Fluke / SKF | https://www.fluke.com/en-gb/product/condition-monitoring/vibration-meters/fluke-805-fc | 2509 | Yes | Annual (calibration) | 7 years | 95 | Fluke official price list 2025 (Ireland/Spain/Netherlands) ? FLUKE-805 FC | Overall vibration measurement on fan motor DE/NDE bearings and fan bearing housing per ISO 10816-3. Classifies vibration as Zone A (new machine), B (acceptable for long-term), C (alarm – investigate), D (danger – stop). Trending over time detects developing bearing defects before failure. FC wireless function logs readings for trending. Also used on escalator motor bearings and pump motor bearings.
13 | HVAC / Air Conditioning | Electronic refrigerant leak detector – F-gas / HFC / HFO – R410A, R32, R407C, R134a | 1 | Inficon TEK-Mate / Testo 316-3 | Inficon / Testo | https://www.inficon.com/en/products/tek-mate-refrigerant-leak-detector | 325 | Yes | Annual (calibration + sensor) | 5 years | 85 | Inficon EU ex-VAT 2024 – TEK-Mate ~€325 | Detection of refrigerant leaks on split AC units and close-control units serving traction substations and signalling rooms. F-gas regulation (EU 517/2014) requires leak check at each service visit and after repair. Detects all HFC/HFO refrigerants including R410A, R32, R407C, R134a at <5 g/year leakage rate. Sensor replacement required every 2 years. Technician must hold F-gas Category I certificate to handle refrigerant.
14 | Lighting Maintenance | Calibrated lux meter – 0.1 to 200,000 lux – EN 12464 station & depot lighting | 1 | Chauvin Arnoux CA 1110 / Konica Minolta T-10MA | Chauvin Arnoux / KM | https://www.chauvin-arnoux.com/en/products/electricity/light-meters/light-meter-ca-1110 | 437 | Yes | Annual (COFRAC) | 7 years | 75 | Chauvin Arnoux official 2026 selection brochure ? CA 1110 at 437 ? HT | Mandatory illuminance verification per EN 12464-1 (indoor workplace lighting) and EN 12464-2 (outdoor). Station platforms require ≥200 lux average, station passages ≥100 lux, depot workshop ≥300 lux, depot exterior ≥20 lux. Used after lamp replacement, luminaire cleaning, or after any modification to the lighting installation. Grid measurement at 0.85m work plane height.
15 | Lighting Maintenance | Telescopic lamp replacement pole set – 2 to 6 m – high-bay luminaire access | 1 | Unger OptiLoc 3-section 6m pole / Ettore Super System pole | Unger / Ettore | https://www.ungerpro.com/en/products/opti-loc-aluminium-extension-pole-6m | 95 | No | Replace if bent | 7 years | — | Unger EU ex-VAT 2024 – ~€95 | Access to depot high-bay LED fittings (6–12 m mounting height) and station platform luminaires without mobile elevated work platforms for routine lamp and driver replacement. Fittings with adapters for tube lamps and recessed downlights. Reduces time for routine PM from >1h (MEWP request) to 15 min for a single fitting. Not suitable for heavy fittings >2 kg or any electrical work.
16 | Consumables / Stock (Team) | Luminaire cleaning kit – IPA wipes + microfibre + soft brush + degreaser – PM cleaning | 2 | 3M cleaning wipes + Würth microfibre + Unger brush | Various | https://uk.rs-online.com/web/c/electronics-cleaning/ | 35 | No | N/A (consumable) | N/A | — | RS / Würth EU ex-VAT 2024 – ~€35 kit | Preventive maintenance cleaning of luminaire diffusers, reflectors, and lens surfaces. Dust and insect accumulation on diffusers reduces lux output by 10–30% over 12 months. IPA wipes for glass/polycarbonate lenses (removes grease and traffic film). Soft brush for louvres and grilles. Performed at each PM visit aligned with lamp replacement or annual inspection cycle.
17 | Tunnel Ventilation | Non-contact tachometer – 10–100,000 RPM – fan speed measurement | 1 | Fluke 930 | Fluke | https://www.fluke.com/en-us/product/building-infrastructure/hvac-tools/fluke-930 | 475 | Yes | Annual (calibration) | 7 years | 45 | Fluke US official retail $512.99 for Fluke 930; converted indicative ex-VAT estimate for EU workbook | Verification of fan rotational speed against VFD-commanded frequency and design nominal RPM. Detects belt slip (for belt-drive fans) or coupling slip (direct-drive). Reflective tape applied to shaft/coupling for optical reading. Also used to confirm fan is fully stopped before opening access panels (safety check). Compared against nameplate RPM and current VFD output frequency.
18 | Tunnel Ventilation | Belt tension gauge (sonic) – poly-V and flat belts – belt drive fans | 1 | Gates Sonic Tension Meter 507C / Burroughs BT-33-73F | Gates / Burroughs | https://www.gates.com/us/en/resources/tools/belt-tension-tool.html | 285 | No | Annual (calibration) | 7 years | — | Gates EU ex-VAT 2024 – 507C ~€285 | Non-contact measurement of belt tension by detecting natural frequency with a pluck. Converts frequency to belt tension in Newtons and compares to manufacturer specification. Under-tensioned belts slip and overheat. Over-tensioned belts accelerate bearing wear. Used at each PM on belt-drive ventilation fans and any HVAC unit with belt-drive AHU. Essential to maintain belt life and fan efficiency.
19 | Tunnel Ventilation | Fan bearing grease gun – high-pressure + IP-rated nozzle + grease cartridge | 1 | Lincoln Industrial 1162 + SKF LGEP 2 grease | Lincoln Industrial / SKF | https://uk.rs-online.com/web/c/pneumatic-tools-power-tools/grease-guns/ | 95 | No | Replace seals every 2 yrs | 5 years | — | Simulator baseline aligned with Lincoln Industrial 1162 grease gun logic | Re-lubrication of fan motor bearings and fan shaft bearings at PM intervals defined by manufacturer (typically 2,000–8,000 hours). Over-lubrication as damaging as under-lubrication – grease gun with pressure gauge preferred. SKF LGEP 2 high-load grease suitable for motor and fan bearings. Apply calculated quantity per bearing volume chart from OEM manual. Clean excess grease after application.
20 | HVAC / Air Conditioning | Digital thermometer + 4 K-type probes – supply/return air, pipe surface, ambient | 1 | Testo 176-T4 4-channel logger / Fluke 52 II | Testo / Fluke | https://www.testo.com/en-GB/testo-176-t4/p/0572-1767 | 285 | Yes | Annual (calibration) | 7 years | 65 | Testo EU ex-VAT 2024 – 176-T4 ~€285 | Temperature measurement across HVAC and heating domains – single instrument replaces a separate heating thermometer. HVAC uses: supply/return air ΔT (typically 6–12°C cooling coil), refrigerant suction/discharge pipe surface (superheat/subcooling estimation), technical room ambient (traction substation limit 35–40°C, signalling room 20–26°C). Heating uses: K-type clamp probe on flow/return pipes to verify boiler ΔT (typically 10–20°C at design load), identifying balancing faults and short-circuit flow paths. 4 simultaneous channels allow flow + return + ambient + reference in one reading.
21 | HVAC / Air Conditioning | Digital thermo-hygrometer – 0–100% RH – humidity check in technical rooms | 1 | Testo 610 / Rotronic HC2-S | Testo / Rotronic | https://www.testo.com/en-GB/testo-610/p/0560-0610 | 125 | Yes | Annual (calibration) | 5 years | 45 | Testo EU ex-VAT 2024 – 610 ~€125 | Relative humidity monitoring in signalling rooms (target RH 45–65% to prevent condensation on PCBs), traction substations (limit typically <70% RH), and HVAC plant rooms. Excessive humidity triggers corrosion on busbars and electronic equipment. Also used to verify dehumidifier performance and to assess comfort conditions in depot offices served by HVAC.
22 | HVAC / Air Conditioning | Differential pressure gauge 0–2,500 Pa – filter ΔP and duct pressure measurement | 1 | testo 512-1 | Testo | https://www.testo.com/nl-NL/testo-512-1/p/0563-1512 | 457 | Yes | Annual (calibration) | 7 years | 45 | Testo official NL store ? testo 512-1 at 457 ? ex VAT | Measurement of filter pressure drop on AHUs and HVAC units to determine when filters require replacement. Typical clean filter ΔP: 30–80 Pa; replacement threshold: 150–250 Pa (per manufacturer spec). Also used to measure duct static pressure for airflow verification. Prevents running clogged filters that overload the fan motor and degrade air quality in technical rooms.
23 | Consumables / Stock (Team) | Air conditioning filter set – G4/F7 class – PM replacement stock (10 units) | 10 | EU7 panel filter 490×490×96mm / EU4 pre-filter – standard HVAC sizes | Various HVAC suppliers | https://uk.rs-online.com/web/c/hvac-r/air-filters/ | 180 | No | N/A (consumable) | N/A | — | HVAC supplier EU ex-VAT 2024 – ~€18/filter avg | PM stock for filter replacement on technical room split AC units and close-control precision cooling. G4/F7 classification per EN 779. Replaced at ΔP threshold or at maximum 6-month interval regardless of ΔP. Signalling rooms and traction substations require F7 minimum to protect electronics from dust. Stocking minimum 10 units covers one PM campaign across multiple technical rooms.
24 | Heating Systems | Manometer set 0–10 bar – heating circuit pressure check + filling station connection | 1 | Rothenberger RO-P1 set / Watts manometer test kit | Rothenberger / Watts | https://www.rothenberger.com/en_GB/products/measuring-and-testing/pressure-gauges | 85 | Yes | Annual (calibration) | 7 years | 35 | Rothenberger EU ex-VAT 2024 – ~€85 set | Static pressure check on heating hydronic circuits (target 1.0–2.0 bar cold fill pressure). Identifies circuit pressure loss (leak or expansion vessel failure). Used with filling station to repressurise system after maintenance. Connected at system drain cock or via Schrader valve on expansion vessel. Essential at each heating PM inspection and after any pipe joint work.
25 | Consumables / Stock (Team) | Water treatment test kit – pH, inhibitor concentration, hardness, chloride – closed circuit | 1 | Fernox Express Test kit / Sentinel X800 test kit | Fernox / Sentinel | https://www.fernox.com/en-gb/products/test-and-monitor/express-test-kit/ | 95 | No | N/A (consumable kit) | Annual | — | Fernox EU ex-VAT 2024 – ~€95/annual kit | Annual water quality check on heating closed circuits at depot. Target: pH 7.5–8.5, inhibitor concentration within manufacturer range, chloride <50 ppm, hardness <200 ppm. Degraded water causes internal corrosion (magnetite sludge) that blocks radiators and heat exchangers. Kit provides test strips + reagents for on-site analysis. Results recorded for CMMS trend and trigger for inhibitor dosing or full system flush.
26 | Escalators | EN 115 clearance gauge card set – step/skirt gap, comb plate, handrail entry | 1 | Custom GO/NO-GO card set to EN 115-1 clearances | Internal workshop / OEM dimensions |  | 60 | No | Annual (dimensional check) | 5 years | — | Workshop-made laminated gauge card set; internal planning estimate | Mandatory clearance checks per EN 115-1:2017 (Safety of escalators and moving walks). Checks: step-to-skirt panel gap ≤4 mm (EN 115 §5.11.2), comb plate tooth clearance ≤6 mm depth, handrail entry guard gap ≤8 mm. GO/NO-GO card gauges for rapid field verification during monthly safety inspections. Any out-of-tolerance reading triggers immediate intervention and out-of-service until corrected.
27 | Consumables / Stock (Team) | Step chain lubricant + precision applicator brush set – escalator PM | 4 | Mobil Extra Hecla Super Grease / KONE Escalator Chain Oil + applicator | Mobil / OEM | https://uk.rs-online.com/web/c/adhesives-sealants-maintenance-chemicals/lubricants/ | 75 | No | N/A (consumable) | N/A | — | RS Components / OEM EU ex-VAT 2024 – ~€75 kit | Step chain lubrication at PM intervals (typically every 1,000 operating hours or 3 months per EN 115 maintenance programme). Correct lubricant viscosity is OEM-specified – incorrect lubricant attracts dust (thick grease) or runs off (too thin). Precision brush applicator reaches pins and rollers without excess. Over-lubrication contaminates steps and floor levels causing slip hazard. Quantity per chain determined by OEM lubrication chart.
28 | Plumbing & Sump Pumps | Water pressure test gauge 0–16 bar + flexible hose + fittings – pipe pressure test | 1 | Rothenberger pressure test kit / Watts FP pressure gauge kit | Rothenberger / Watts | https://www.rothenberger.com/en_GB/products/pipe-installation/pressure-testing | 125 | Yes | Annual (calibration) | 7 years | 35 | Rothenberger EU ex-VAT 2024 – ~€125 kit | Hydraulic pressure testing of repaired pipe joints, valve replacements, and new pipework at depot. BS EN 806 requires cold water systems tested to 1.5× working pressure for minimum 1 hour. Identifies micro-leaks at solder joints, compression fittings, and WRAS-approved push-fit connections. Records test pressure and duration in CMMS as evidence of compliance. Used after any pipe repair or new connection.
29 | Plumbing & Sump Pumps | Digital sump level probe + float switch tester – pump auto-start level verification | 1 | WIKA level probe / Gems Sensors float switch tester | WIKA / Gems | https://www.wika.com/en_GB/products/level-measurement/ | 185 | Yes | Annual (calibration) | 7 years | 55 | WIKA EU ex-VAT 2024 – ~€185 | Verification of sump pump auto-start and auto-stop float switch levels during PM inspections. Tests pump starts at correct level (not too high – risk of overflow; not too low – dry running). Measures actual water depth against switch activation point. Also confirms alarm float level is set above auto-start (high-water alarm before sump overflows). Used at each 6-monthly PM inspection on all depot drainage sump pumps.
30 | Consumables / Stock (Team) | PTFE thread tape + pipe jointing compound + compression fitting kit – plumbing repair | 2 | Henkel LOCTITE 55 thread seal / Würth jointing compound + copper fitting assortment | Henkel / Würth | https://uk.rs-online.com/web/c/plumbing-hvac/pipe-fittings/ | 55 | No | N/A (consumable) | N/A | — | RS / Würth EU ex-VAT 2024 – ~€55 assortment | Sealing and repair of threaded and compression joints on depot plumbing (cold/hot water, compressed air, heating flow/return). PTFE tape for parallel threads; LOCTITE 55 for tapered fittings up to G2 BSP. Compression fitting assortment covers 15mm to 35mm OD copper pipe for emergency repairs. Used at Level 2 corrective maintenance – full repipe at Level 3 requires planned shutdown.
31 | Consumables / Stock (Team) | Asset identification labels – polyester self-laminating – heat/oil/UV resistant | 1 | Brady BMP61 polyester label roll / HellermannTyton TT4-108 | Brady / HellermannTyton | https://www.bradyid.eu/en-eu/product-lines/bmp61-label-printer/ | 55 | No | N/A (consumable) | N/A | — | Brady EU ex-VAT 2024 – ~€55 roll | Equipment identification labelling for all MEP assets: fan units (FAN-TUN-01 etc.), luminaire circuits (LTG-PLT-A01), escalator identification (ESC-01), HVAC units (HVAC-SR-01), sump pumps (PMP-DEP-01). Self-laminating polyester resists moisture, oil, and 120°C heat. Essential for CMMS asset tracking and for ensuring correct isolation of the intended equipment during LOTO.
32 | Consumables / Stock (Team) | Cable ties assorted + cable labels + heat-shrink sleeves – wiring identification | 1 | Panduit KP-HSTT1 heat-shrink kit + HellermannTyton T18R ties + self-laminating cable labels | Panduit / HellermannTyton | https://www.newark.com/panduit/kp-hstt1/heat-shrink-tubing-assortment/dp/39C2377 | 135 | No | N/A (consumable) | N/A | — | Simulator baseline aligned with AFC wiring rework consumable kit | Cable management and labelling after maintenance interventions on all MEP systems. Replacement of broken cable ties in fan terminal boxes, HVAC control panels, and escalator drive cabinets. Heat-shrink for protection of repaired terminations. Alphanumeric labels identify modified cables for CMMS traceability. Essential for maintaining the integrity of wiring modifications and ensuring future maintenance personnel can follow the installation.
33 | Electrical Measurement | Three-phase rotation tester 40-700V AC ? motor phase-sequence verification before start-up | 1 | Fluke 9040 | Fluke | https://www.fluke.com/en/product/electrical-testing/basic-testers/fluke-9040 | 316 | Yes | Annual (calibration) | 10 years | 75 | Simulator archive baseline aligned with Fluke 9040 | Verification of phase sequence after reconnection or motor replacement on tunnel fans, sump pumps, HVAC compressors and any 3-phase rotating equipment. Prevents reverse rotation, wrong air direction, pump no-flow condition and mechanical damage at first energisation.
34 | Electrical Measurement | Multifunction installation tester ? RCD, loop impedance, continuity, insulation ? LV lighting and socket circuits | 1 | Fluke 1664 FC Multifunction | Fluke | https://media.fluke.com/4505bf82-3ba6-413d-b84b-b10800c11e39_original%20file.pdf | 1998 | Yes | Annual (calibration) | 10 years | 145 | Simulator archive baseline aligned with Fluke 1664 FC | Commissioning and post-maintenance verification of LV lighting boards, technical-room auxiliaries, small power circuits and modified final circuits. Confirms protective conductor continuity, loop impedance, RCD tripping and core IEC 60364 / NF C 15-100 compliance before return to service.
35 | Advanced Diagnostics | Infrared thermometer -30 to +650 C ? quick thermal screening of motors, panels and bearings | 1 | Fluke 62 MAX+ | Fluke | https://www.fluke.com/fr-fr/produit/thermometres/thermometres-infrarouges/fluke-62-max | 148 | Yes | Annual (check) | 8 years | 35 | Simulator baseline aligned with Fluke 62 MAX+ | Quick first-line thermal screening of fan bearings, pump motors, escalator drives, HVAC compressors, electrical terminals and lighting panels. Used for routine PM and fault triage when a full thermal camera survey is not justified.
36 | Workshop / Team | Fine-range torque wrench 5-25 Nm with removable ratchet ? controlled tightening on terminals and small assemblies | 1 | Facom R.306A25 | Facom | https://www.facom.com/GLOBALBOM/XJ/E.306A200S/1/Instruction_Manual/EN/E.306_T1_EUR.pdf | 155 | Yes | Annual (COFRAC calibration) | 10 years | 45 | Simulator baseline aligned with Facom R.306A25 | Controlled tightening of terminal blocks, contactors, breaker terminals, VFD auxiliaries, HVAC electrical accessories and small mechanical fasteners where under-torque causes overheating and over-torque damages threads or housings.
37 | Refrigeration & HVAC (Team) | Refrigerant recovery unit 230V oil-less ? recovery before opening HVAC/refrigeration circuits (conditional) | 1 | Robinair RG3-230 / Rothenberger ROREC PLUS 230V | Robinair / Rothenberger | https://www.robinair.com/products/rg3-portable-refrigerant-recovery-machine-230v | 895 | No | Annual (inspection) | 7 years | ? | Official product page; planning estimate for compact 230V recovery unit | Only required if the MEP team opens refrigerant circuits internally at Level 3. Used to recover refrigerant before replacing compressors, valves, driers or other sealed-circuit components, in line with F-gas containment and recovery obligations. Not required if all sealed-circuit opening remains outsourced.
38 | Refrigeration & HVAC (Team) | Refrigerant recovery cylinder dual-valve 27 L / 12.5 kg ? dedicated recovered refrigerant bottle (conditional) | 1 | REFCO REF-CYL / equivalent EN 13322-1 recovery cylinder | REFCO / HVAC-R supplier | https://www.refco.ch/40%20Dokumente%20Produkte/20_Bedienungsanleitungen/REF-CYL-Manual/4686959_REF-CYL_Manual_en.pdf | 240 | No | Periodic inspection / recertification | 10 years | ? | REFCO recovery cylinder family documentation; planning estimate for 27 L dual-valve bottle | Only required if refrigerant is recovered in-house. Dedicated recovery cylinder used with the recovery unit to receive recovered refrigerant safely, avoid venting and maintain traceability of recovered charge.
39 | Refrigeration & HVAC (Team) | Nitrogen pressure/leak test set 0-50 bar ? regulator, hose and bottle connection for HVAC circuits (conditional) | 1 | ROTHENBERGER Nitrogen Set 1000003865 | ROTHENBERGER | https://rothenberger.com/ch-it/kit-azoto/set-di-azoto-per-circuiti-di-refrigerazione-per-la-germania-1000003865 | 425 | No | Annual (inspection) | 7 years | ? | ROTHENBERGER official nitrogen set product page; planning estimate | Only required if the MEP team performs sealed-circuit repairs internally. Used for dry pressure testing, leak testing, line flushing and nitrogen purge during brazing on refrigeration and air-conditioning circuits.
40 | Heating (Team) | Combustible gas leak detector ? methane / propane local leak search on gas train and fittings (conditional) | 1 | ROTEST Electronic 4 complet 1000003199 | ROTHENBERGER | https://rothenberger.com/fr-fr/produits/appareils-de-detection-des-fuites-pour-conduites-de-gaz/rotest-electronic-4-complet-1000003199 | 285 | Yes | Annual (functional check / calibration) | 5 years | 65 | ROTHENBERGER official product page; planning estimate | Only required if the MEP team carries out internal Level 2-3 maintenance on gas-fired heating equipment. Used for local leak search on valves, unions, regulators, burner trains and accessible gas pipework. Not necessary if all gas interventions remain outsourced.

## Project MEP
No. | Category | Tool Description | Qty / Team | Reference | Supplier | Product URL | Unit Price (€ ex-VAT) | Calibration | Frequency | Lifespan | Calib. Cost (€/yr) | Price Source | Detailed Usage
1 | Advanced Measurement | Thermal imaging camera 320×240 – hot spots on motors, panels, connections | 1 | TiS60+ | Fluke | https://www.fluke.com/fr-fr/produit/cameras-thermiques/fluke-tis60-plus | 3812 | Yes | Annual (calibration) | 10 years | 285 | Simulator baseline aligned with Fluke TiS60+ | Level-2 thermographic inspection across all MEP domains: fan motor hot spots and bearing overheat (>80°C alarm on motor frame), lighting panel loose connections (temperature differential >15°C vs adjacent), escalator traction motor and brake, HVAC compressor/condenser, substation traction equipment, and heating distribution manifolds. Annual thermographic survey of all LV distribution boards is best practice (BS 7671 / IEC 60364). Reports exported and archived in CMMS.
2 | Advanced Measurement | 3-axis vibration analyser + accelerometer + data collector – ISO 10816 Level 2-3 | 1 | Fluke 810 Vibration Tester | Fluke | https://www.fluke.com/en-gb/product/condition-monitoring/vibration-testers/fluke-810 | 13084 | Yes | Annual (calibration) | 10 years | 385 | Fluke official price list 2025 ? FLUKE-810 | Full spectrum vibration analysis on tunnel ventilation fans (imbalance, misalignment, looseness, bearing defect frequency analysis), escalator traction motors, and large sump pumps. Goes beyond the technician vibration meter: FFT spectrum analysis identifies specific fault frequencies (BPFO, BPFI, FTF, BSF for bearings). Routes programmed for all fan and pump locations. Trending database detects developing faults 4–8 weeks before failure enabling planned replacement.
3 | Advanced Measurement | Clamp-on ultrasonic flow meter – non-invasive – heating and water circuits | 1 | Fuji Portable Ultrasonic Flowmeter FSC | Fuji Electric | https://americas.fujielectric.com/products/instrumentation/flow-meters/portable-ultrasonic-flowmeter-fsc/ | 2850 | Yes | Annual (calibration) | 10 years | 285 | Fuji official FSC product page; Portaflow X removed because discontinued, price kept as planning estimate | Non-invasive flow measurement on heating circuits (balancing verification), domestic cold/hot water mains (leak detection by comparison), and sump pump discharge. Clamps externally on pipe 15–1200mm OD without cutting in. Used to verify boiler flow rates against design, to confirm sump pump output meets specification, and to detect hidden leaks by comparing flow at two points. No pipe isolation required.
4 | Ventilation & Air Balancing | Airflow capture hood (balancing hood) – 0.05–5 m³/s – grille flow measurement | 1 | TSI Alnor EBT731 | TSI | https://tsi.com/products/ventilation-test-instruments/alnor/alnor-capture-hoods/alnor-balometer-capture-hood-ebt731 | 1830 | Yes | Annual (calibration) | 7 years | 145 | TSI official EBT731 model page + distributor market price for base kit | Air volume flow measurement at supply and extract grilles/diffusers in station and depot. Used for commissioning verification and rebalancing after filter replacement, duct modification, or fan change. Hood placed over grille; integral micromanometer displays flow in m³/s or l/s. EN 12599 recommends balancing at commissioning and after modifications. Essential for verifying ventilation rates in traction substations (heat dissipation) and signalling rooms (equipment cooling).
5 | Ventilation & Air Balancing | Laser shaft alignment tool – fan-motor alignment check – coupling and belt drives | 1 | FLUKE-830 | Fluke | https://www.fluke.com/en-gb/product/condition-monitoring/shaft-alignment/fluke-830 | 7453 | Yes | Annual (calibration) | 10 years | 285 | Fluke official price list 2025 ? FLUKE-830 | Precision shaft alignment of fan-motor couplings after motor or bearing replacement. Misalignment is the primary cause of premature bearing failure and vibration on fan units. Laser alignment achieves angular and offset misalignment <0.02 mm – unachievable with dial gauges at this speed. Simultaneous display of soft foot, angular and offset misalignment in horizontal and vertical planes. Also used on large pump motor couplings at depot.
6 | Heating (Team) | Combustion flue gas analyser – O₂, CO, CO₂, efficiency – gas boiler tuning | 1 | Testo 330-2 LL / Kane 257 flue gas analyser | Testo / Kane | https://www.testo.com/en-GB/testo-330-2-ll/p/0632-3307 | 1485 | Yes | Annual (calibration) | 7 years | 145 | Testo EU ex-VAT 2024 – 330-2 LL ~€1485 | Level 2–3 gas boiler tuning and annual service. Measures flue gas CO, CO₂, O₂, temperature, and calculates combustion efficiency and excess air ratio. Confirms CO <10 ppm (combustion quality) and efficiency >88% (gas boiler minimum). UK Gas Safe / FR Qualigaz mandatory for gas work beyond Level 1. Used at annual boiler service, after burner component replacement, and whenever combustion efficiency alarm is raised by BMS.
7 | Plumbing (Team) | Pipe inspection camera / CCTV endoscope 30m cable – drain and buried pipe survey | 1 | Ridgid SeeSnake Compact2 / Wohler VIS 250 inspection camera | Ridgid / Wohler | https://www.ridgid.com/eu/en/seesnake-compact2 | 2850 | No | Annual (inspection) | 7 years | — | Ridgid EU ex-VAT 2024 – SeeSnake Compact2 ~€2850 | Visual inspection of buried and concealed drainage pipes at depot, sump pump discharge lines, and underground water mains to identify blockage origin, pipe condition, and collapse without excavation. 30m cable with 40mm camera head navigates 100mm–200mm pipes. Self-levelling camera head maintains upright image. Used for scheduled 5-year drain surveys per BS EN 13508, for post-blockage investigation, and pre-repair condition survey to justify excavation.
8 | Safety / Confined Space (Conditional) | Confined-space tripod + winch + retrieval set ? sump / pit / shaft rescue standby (conditional) | 1 | 3M DBI-SALA tripod / winch / retrieval set | 3M DBI-SALA | https://www.3m.com/3M/en_US/p/d/v101679053/ | 2950 | Yes | Annual (inspection by competent person) | 10 years | 185 | 3M DBI-SALA official confined-space tripod/winch system page; planning estimate for complete rescue set | Only required if entry into pits, shafts, wet wells or similar confined spaces is authorised in the MEP maintenance concept. This is not a work-at-height convenience item; it is rescue standby equipment that must be available before entry. If the operating rule is strict no-entry, this line should be removed.